## Tabelle1
Energy field |  | Observation criteria | Found in factory? (Yes/No) | Areas in factory, remarks |  | Possible measures | Next steps
Compressed air | Is the air intake of the compressor exposed to heat or direct sun? |  |  |  | Note: hot air intake increases energy consumption of compressor
§ Install covers to protect from sun
§ Re-arrange air intake
| Are air- and oil-filters dirty? |  |  |  | § Clean / replace filters
§ Establish regular checks (at least once in 6 months)
| Have you found any leaks, e.g. by fizzling noises? |  |  |  | § Conduct systematic leakage detection and fix leaks immediately
§ Establish procedure for regular leakage detection, at least once in 6 months
| Is the pressure level above 6 bar? |  |  |  | Note: Reducing system pressure by just 1 bar achieves energy savings of 6-10%.
§ Start a process to reduce pressure level stepwise to an optimized level which still ensures proper working of compressed air tools
| Does the pressure drop between compressor and any point of use in the factory exceed 1 bar? |  |  |  | § Investigate sources for pressure drop, esp.:
- excessive use of spiral hoses instead of proper pipework
- undersized pipework
- sharp bends of air lines
- inconsistent diameters of couplings
- cheap connections and valves
§ Check upgrading the single line system to a ring line system (= loop back to compressor) to reduce pressure drop
| Are there any valves left open when there is no use of compressed air? |  |  |  | § Instruct staff to close valves
§ Place signs to increase awareness
| Are there any areas in the factory that do not permanently need compressed air, e.g. during night shift? |  |  |  | § Install additional valves to close those areas
§ Establish procedures for closing lines, e.g. during night shifts or times of low production
| Have you found any broken or damaged blow guns in use? |  |  |  | § Replace damaged blow guns immediately. Use low-pressure ones (3 bar)
| Are blow guns working with full pressure level instead of low pressure? |  |  |  | § Replace them by low-pressure guns (3 bar) or install pressure valve at the gun to reduce pressure level of blow gun
Hydraulic processes | Have you found any oil leak found or traces of oil which results from leakages? |  |  |  | § Conduct systematic leakage detection of hydraulic equipment and fix leaks immediately
| Have you found hydraulic pumps / system still working even they are not in use? |  |  |  | § Establish procedures to switch off hydraulic pumps when not needed
§ Place signs to increase awareness
| Have you found obvious air bubble in hydraulic pipes? |  |  |  | § Refill oil
§ Establish regular maintenance checks for hydraulic equipment
Process Heat | Boiler: Has been found scaling or fouling / soot in boiler? |  |  |  | Note: these deposits from water / flue gas cause additional energy use
§ Remove scale and soot
§ Establish regular inspections
§ Install an automatic blowdown system (= sensor controlled unit to remove solids in hot water)
| Are there any steam lines or pipes for hot water not being properly insulated? |  |  |  | § Install proper insulation at all lines
§ Improve insulation
| Is there any damaged insulation at pipes or boiler? |  |  |  | § Repair insulation
| Are there any leaks in steam lines? |  |  |  | § Fix leaks immediately
§ Establish procedure for regular leakage detection
| Are there any valves left open when there is no use of steam or hot water? |  |  |  | § Instruct staff to close valves
§ Place signs to increase awareness
| Are there areas, workplaces or machines where steam or hot water still runs through even it is not in use, e.g. left workplaces in ironing area? |  |  |  | § Establish procedures to switch off heating equipment when not needed
§ Place signs to increase awareness
§ Analyse processes to eliminate idle running
| Is there any possibility to recover waste heat, condensate, or hot rinse water, e.g. condensate from ironing section? |  |  |  | § Conduct an investigation of hot-spots for making use of heat recovery in factory
§ Evaluate all hot streams of releasing heat and required heat in the factory to identify suitable options for heat recovery
| Stenter: are filters at stenters covered with dirt and dust? |  |  |  | § Clean / Replacing filters
§ Establish regular maintenance for filters
Electric motors | Have you found motors covered with dirt and dust, especially at the radiator? |  |  |  | § Clean motors
§ Establish regular cleaning (once a year)
| Have you found any slack belts at motors? |  |  |  | § Replace / tighten belt
§ Establish regular maintenance checks
| Have you found any machinery idle running for example during lunch breaks? |  |  |  | § Establish procedures to switch off equipment when not needed
§ Place signs to increase awareness
§ Analyse processes to eliminate idle running
| Are there motors where a Variable Speed Drive (VSD) could optimize variable load of the motor? |  |  |  | A VSD is an electronic control to adjust electrical supply precisely to actual need when speed or torque change, especially suitable for presses, pumps, conveyors, buffing, grinding, brushing machines
§ Establish a policy to consider Variable Speed Drive (VSD) / inverters when purchasing motors and machinery.
§ Equip motors which are operated under varying speed / torque with a VSD
| Are there any motors that will be replaced or purchased in the next months, e.g. motors of sewing machines? |  |  |  | § Apply a policy to purchase efficient motors with energy efficiency label
§ Purchase servo-motors for sewing machines
§ Evaluate the use of a Variable Speed Drive (VSD)
Lighting | Are lights left switched-on in areas not being occupied? |  |  |  | § Instruct staff to switch-off lights
§ Place signs for staff
§ Install sensors in less frequented areas, e.g. wash-rooms, storage area
| Are there areas where additional light switches or re-arrangement of lights would save electricity? |  |  |  | § Install additional light switches for certain zones in an area
§ Install individual lights for workplaces
| Have you found lights covered with dust? |  |  |  | § Clean lights
| Is there any area where installation of energy efficient lights (e.g. LED’s) can be started within the next months? |  |  |  | § Starting with installation of LED’s in one area, especially when refurbishment is planned anyway
§ Install proper reflectors in order to minimize diffusive light
AC / Air Conditioning | Are doors and windows left open when heating/cooling is switched on? |  |  |  | § Instruct staff
§ Place signs for staff
| Are rooms cooled to lower temperature level than necessary (for example below 23°C)? |  |  |  | Note: every 1°C less cooling effort saves 10% of energy used for AC
§ Reset AC
§ Place signs for increasing awareness not to cool lower than necessary
| Are thermostats for AC exposed to direct sun or heat sources? |  |  |  | § Thermostats that are exposed to direct sun or heat cause unnecessary cooling work of AC
§ Relocate thermostats
§ Protect thermostats from direct sunlight
General | Is there any damaged equipment or equipment where maintenance seems to be neglected? |  |  |  | § Set-Up / revise maintenance plan
§ Establish regular maintenance procedures
| Is there any new arrangement of workplaces, machinery, floors planned in the next time? |  |  |  | § Evaluate opportunities for energy efficient equipment
§ Make an investment plan for purchasing efficient equipment
| Is there any equipment that will be purchased soon, e.g. compressed air devices, ironing tables, pumps etc.? |  |  |  | § Set-up a purchasing policy for energy efficient equipment
§ Consider energy costs into investment decisions
| Is there any possibility to install photovoltaics (PV) or other renewable energy sources for electricity generation? |  |  |  | § Evaluate feasibility for installment
CLIMATE ACTION TRAINING FOR TEXTILE SUPPLIERS IN VIETNAM - ENERGY SAVING WALK AROUND
Identify Areas for Evident Energy Savings by a Walk-Around through the Factory.
Please go through all areas and floors in your factory incl. production areas, warehouse, service rooms etc.
Check those areas according to the given observation criteria. In case, any issue has been found during your walk around, mark it with "YES".
Document also, where in the factory you have found it.
Any criteria that is market with "YES", means there is evident need for taking energy saving measures. You'll find some proposals in column 4 ('Possible measures').
After completing the Walk-Around, define next steps for improvement incl. a timeline.